## VAV
VAV BOXES | [16 empty] | ADDITIONAL COMMENTS ON SELECTION
# | MANUF | MODEL | LOCATION | SERVES | SIZE INLET | CFM |  | FAN (HP) | SP INLET | KW | ELECTRICAL |  | LWA (SNS) | WT | ISOLATION | NOTES
[6 empty] | MIN | MAX |  |  |  | V / PH | FLA
NOTES: 1. RUN CONTINUOUS 2. PROVIDE W/ SPEED CONTROLLER

## WSHP
WATER SOURCE HEAT PUMP
# | MANUF | MODEL | LOCATION | SERVES | CFM | OSA | ESP ("WC) | GPM | HEATING |  | COOLING |  | ELECTRICAL |  |  |  | WT (LBS) | LWA | ISO | NOTES | AUX HEAT SIZING CALC FOR OSA ELECTRIC HEATING DURING DEFROST CYCLE
[9 empty] | MBH | HSPF (COP) | TONS | SEER (EER) | V/PH | AUX KW | MCA | MOCP |  |  |  |  | OUTSIDE TEMP | DISCHARGE TEMP | DERATE 208V=.89 460v=1 | BTU/KW | TON/KW | MIN RATED KW
[21 empty] | 19 | 65 | 0.89 | 3413 | 3.5 | 0
NOTES: 1. W/ HONEYWELL PRO 8000 TSTAT 2. UNIT MOUNTED ON CURB 3. AUXILARY ELECTRIC HEAT IN UNIT 4. UNIT MOUNTED ON SPRING ISOLATION CURB, CURB INFILLED WITH BATT INSULATION (BY OTHERS) 5. W/ 100% OUTSIDE AIR HOOD 6. W/ ECONOMIZER HOOD
Note on F4: Eric Peterson: ABOVE 2000 CFM NEEDS DUCT SMOKE ALARM

## BC
VRF BRANCH CONTROLLER
# | MANUF | MODEL | LOCATION | SERVES | # OF PORTS | ELECTRICAL |  |  | WT | NOTES
[6 empty] | VOLT | MCA | MOCP
NOTES: 1. CONDENSATE PIPING BY OTHERS. 2. CONDENSATE PIPING BY EAI. PLUMBER TO PROVIDE DRAIN RECEPTACLE WITHIN 50' 3. INSTALL BALL VALVES ON PORTS
| MITSUBISHI | CMB-P105NU-G |  |  | 5 | 208/1 | 0.4 | 15 | 72 |  | SINGLE BC, FOR USE W/O SUB AND <126MBH
| MITSUBISHI | CMB-P106NU-G |  |  | 6 | 208/1 | 0.5 | 15 | 72 |  | SINGLE BC, FOR USE W/O SUB AND <126MBH
| MITSUBISHI | CMB-P108NU-G |  |  | 8 | 208/1 | 0.7 | 15 | 84 |  | SINGLE BC, FOR USE W/O SUB AND <126MBH
| MITSUBISHI | CMB-P1010NU-G |  |  | 10 | 208/1 | 0.8 | 15 | 94 |  | SINGLE BC, FOR USE W/O SUB AND <126MBH
| MITSUBISHI | CMB-P1013NU-G |  |  | 13 | 208/1 | 1.08 | 15 | 126 |  | SINGLE BC, FOR USE W/O SUB AND <126MBH
| MITSUBISHI | CMB-P1016NU-G |  |  | 16 | 208/1 | 1.04 | 15 | 138 |  | SINGLE BC, FOR USE W/O SUB AND <126MBH
| MITSUBISHI | CMB-P108NU-HA1 |  |  | 8 | 208/1 | 1.45 | 15 | 124 |  | MAIN BC
| MITSUBISHI | CMB-P1010NU-HA1 |  |  | 10 | 208/1 | 1.6 | 15 | 131 |  | MAIN BC
| MITSUBISHI | CMB-P1013NU-HA1 |  |  | 13 | 208/1 | 1.08 | 15 | 148 |  | MAIN BC
| MITSUBISHI | CMB-P1016NU-HA1 |  |  | 16 | 208/1 | 1.63 | 15 | 172 |  | MAIN BC
POWERED FROM OUTDOOR UNIT AT LINE VOLTAGE BY OTHERS
LINE VOLTAGE CONTROL WIRING FROM OUTDOOR UNIT BY OTHERS
LOW VOLTAGE CONTROL WIRING BY EAI
POWER CONNECTIONS BY OTHERS, SEE SUBMITTALS FOR REQUIREMENTS

## DAMPER
DAMPERS *GENERIC SCHEDULE, ADDITIONAL ITEMS NOT INDICATED ON PLANS/SUBMITTALS SHOWN TO ALLOW FLEXIBILITY FOR FIELD CONDITIONS
TAG | MANUF | MODEL | DESCRIPTION | TYPE | VOLTAGE | NOTES
MD-A | POTTORFF | CD-42 or CD-21R | OPP BLADE CNTRL | CLASS 1A | 24V | 4,6
MD-B | POTTORFF | CD-42 or CD-21R | OPP BLADE CNTRL | CLASS 1A | 120V | 1,5,6
MD-C | POTTORFF | CD-42 or CD-21R | OPP BLADE CNTRL | CLASS 1A | 120V | 1,2,3,5,6
MD-D | POTTORFF | CD-42 or CD-21R | OPP BLADE CNTRL | CLASS 1A | 24V | 5,6,7
MD-E | POTTORFF | CVP SRRD | TRUE RND BFLY CTRL | CLASS 1A | 24V | 5,6,7 | SIMPLE CHEAP 2 POSITION DAMPER FOR ERV LOUVERS AND ZONE CONTROLS ON ROUND DUCT ONLY
CBD-A | POTTORFF | CBD-150 | COUNTERBALANCED |  | N/A | 6
FSD-A | POTTORFF | FSD-142-OP | GRILLE ACCESS FSD | UL555/555S | 120V | 3,6
FSD-B | POTTORFF | FSD-142 | IN WALL FSD | UL555/555S | 120V | 3,6
FSD-C | POTTORFF | FSD-125R | IN WALL TRUE ROUND FSD | UL555/555S | 120V | 3,6
FD-A | POTTORFF | VFD-10-A or VFD-15R | 1.5 HR FIRE DAMPER | UL555 | NA | 6
FD-B | POTTORFF | VFD-30-A | 3 HR FIRE DAMPER | UL555 | NA | 6
FD-C | POTTORFF | VFD-10-TLA | 1.5HR THINLINE FIRE DAMPER | UL555 | NA | 6
SD-A | POTTORFF | SD-142 | SMOKE CONTROL DAMPER | UL555S | 120V | 1,2,3,5
NOTES: TYPICAL ALL, SEE PLANS FOR QUANTITIES AND SIZES. LISTED MODELS ARE RECTANGULAR/ROUND RESPECTIVELY. 1. POWER BY EC 2. WIRED TO BACKUP POWER SOURCE. POWER CLOSED, SPRING OPEN. INCLUDE PI-50 DUAL POS. INDICATOR SWITCH. 3. WIRED TO FA SYSTEM BY OTHERS. 4. 0-10 MODULATING 5. 2 POSITION, (OPEN CLOSE) 6. FIELD VERIFY SIZE AND OPENING PRIOR TO ORDERING 7. POWER OPEN, FAIL CLOSE
requirements for fire dampers and penetrating fire rated walls are located in IBC section 714 and 717
https://codes.iccsafe.org/content/IBC2015/chapter-7-fire-and-smoke-protection-features
Requirements for when a damper to outside needs to be motorized shutoff dampers located in C403.2.4.3. This includes intake exhaust and relief over 300cfm operating intermittantlym, except combustion air and type 1 exhaust.

## ERV
ENERGY RECOVERY VENTILATORS
# | MANUF | MODEL | LOCATION | SERVES | CFM | ESP ("WG) | EFFICIENCY |  | ELECTRICAL |  |  | WT | NOTES
[7 empty] | WINTER | SUMMER
[7 empty] | EFF % | EFF % | VOLT | MCA | MOCP
ERV-1 | MITSUBISHI | LGH-F600RX5-E1 | RETAIL SPACE | RETAIL SPACE | 600 | 0.56 | 64 | 50 | 208/1 | 3.6 | 15 | 132
NOTES: 1. ERV TO RUN VIA SCHEDULE SET USING (SPECIFY A PROGRAMMABLE THERMOSTAT). 2. INTERLOCK WITH LOW VOLTAGE MOTORIZED DAMPERS ON OUTSIDE AIR AND EXHAUST DUCTS. SEE CONTROL DRAWING
diagram saved as pdf on P:\Engineering\Details\DETAIL PDFS\C CONTROLS\LOSSNAYS EXTERNAL SENSOR.pdf
TYPICAL ERV NOTES TO CUT AND PASTE
ERV TO RUN AT LOW SPEED FROM OCCUPANCY SENSOR, RAMP UP TO HIGH UPON SIGNAL FROM CO2 SENSOR.
ERV TO RUN AT LOW SPEED FROM OCCUPANCY SENSOR, RAMP UP TO HIGH FROM MANUAL WALL SWITCH.
ERV TO RUN AT LOW SPEED VIA SCHEDULE SET, RAMP UP TO HIGH ON CO2 SENSOR.
ERV TO RUN AT LOW SPEED VIA SCHEDULE SET, RAMP UP TO HIGH FROM OCCUPANCY SENSOR.
ERV TO RUN VIA SCHEDULE SET.
ERV TO RUN CONTINUOUS AT FULL SPEED.
ERV OPERATES INDEPENDANTLY OF ZONE HEATING AND COOLING EQUIPMENT AS A DEDICATED OUTDOOR AIR SYSTEM (DOAS). ZONE HEATING AND COOLING FANS SHUT OFF IN THE ABSENSE OF A TEMPERATURE CALL FROM TSTAT.
LINE VOLTAGE CONTROLS SHARED BY OTHER AMMENTITIES. FURNISHED AND INSTALLED BY OTHERS.
LOW VOLTAGE CONTROLS FURNISHED AND INSTALLED BY HVAC.
INTERLOCK WITH LOW VOLTAGE MOTORIZED DAMPERS ON OUTSIDE AIR AND EXHAUST DUCTS. SEE CONTROL DRAWING
INSERT LINES WITHIN GRAY ZONE FOR VLOOKUP FUNCTION TO WORK
| LOSSNAY | LGH-F300RX5 |  |  | 300 | 0.5 | 63 | 50 | 208/1 | 1.8 | 15 | 73
| LOSSNAY | LGH-F470RX5 |  |  | 470 | 0.5 | 64 | 51 | 208/1 | 3.1 | 15 | 119
| LOSSNAY | LGH-F600RX5 |  |  | 600 | 0.5 | 64 | 50 | 208/1 | 3.6 | 15 | 132
| LOSSNAY | LGH-F1200RX5 |  |  | 1200 | 0.5 | 64 | 50 | 208/1 | 7.1 | 15 | 265

## FAN
FANS | [15 empty] | ADDITIONAL COMMENTS ON SELECTION
# | MANUF | MODEL | LOCATION | SERVES | DRIVE | DAMPER | CFM | SP (" WC) | HP (W) | ELECTRICAL |  | LWA (SNS) | WT | ISOLATION | NOTES
[10 empty] | V / PH | FLA
NOTES: 1. RUN CONTINUOUS 2. PROVIDE W/ SPEED CONTROLLER
frequently useful notes
smoke pressurization fans are always 3 phase with VFD. If no 3 phase is panel is available we can chang eto a single phase input VFD at the electricians request. EC agrees to cost change.
GARAGE EXHAUST FAN TO RUN ON OCCUPANCY SENSOR FOR 20 MINUTES IN ACCORDANCE WITH WSEC C403.2.6.4.2 EXCEPTION FOR SYSTEMS UNDER 8000 CFM. | [15 empty] | SMALL GARAGE EXHAUST SYSTEM -10% OF THE TIME
GARAGE EXHAUST FAN TO RUN LOW AT 6% CFM OR 20 HRZ, WHICHEVER IS GREATER. FAN TO BE CONTROLLED FROM VFD, SIGNAL PER CO/NO2 SENSOR ARRAY TO RAMP FAN UP TO HIGH OVER A 15 MINUTE PERIOD. SEE DIAGRAM. | [15 empty] | LARGE GARAGE EXAUST FAN -90% OF THE TIME
CONTROLLED VIA LINE VOLTAGE-COOLING ONLY TSTAT. SET TO 80F | [15 empty] | MEP ROOMS WITH FAN COOLING
PROVIDE WITH SWITCH (BY EC)
PROVIDE W/ 1.5X BELTS NEEDED FOR DUTY, CONNECT TO LEGALLY REQUIRED STANDBY POWER. INTERLOCK WITH FIRE ALARM SYSTEM BY OTHERS. W/ (#) DUCT SMOKE DETECTORS (WIRED TO SHUT DOWN), INSTALLED BY MC. VFD PROVIDED FOR BALANCING. FIRE ALARM SYSTEMS MONITORS FAN OPERATION FROM VFD. | [15 empty] | PRESSURIZATION FAN
FAN TO RAMP UP TO HIGH ON CO2 [OR] OCCUPANCY SENSOR FOR VENTILATION, IN LEIU OF ERV PER 2015 SEATTLE ENERGY CODE SECTION C403.6.1 EXCEPTION 1 | [15 empty] | OSA FANS WHERE ERVS ARE OTHERWISE REQUIRED TO BE DOAS TO GET THE ECONOMIZER EXCEPTION
CONTROLLED VIA LINE VOLTAGE-COOLING ONLY TSTAT. SET TO TURN ON AT 80F, TURN OFF AND TRIGGER ALARM AT 140F. | [15 empty] | SCL VAULT
INSERT LINES WITHIN GRAY ZONE FOR VLOOKUP FUNCTION TO WORK
| TD-100 | S&P |  |  | DD |  | 57 | 0.25 | (26) | 120/1 |  | N/A | 2 | RUBBER GROMMET | 2 | always use a speed controller with these to dial them in
| TD-100X | S&P |  |  | DD |  | 53 | 0.37 | (33) | 120/1 |  | N/A | 5 | RUBBER GROMMET | 2 | always use a speed controller with these to dial them in
| TD-125XS | S&P |  |  | DD |  | 33 | 0.5 | (36) | 120/1 |  | N/A | 12 | RUBBER GROMMET | 2 | always use a speed controller with these to dial them in
| TD-150S | S&P |  |  | DD |  | 257 | 0.5 | (65) | 120/1 |  | N/A | 14 | RUBBER GROMMET | 2 | always use a speed controller with these to dial them in
| TD-200S | S&P |  |  | DD |  | 415 | 0.5 | (122) | 120/1 |  | N/A | 20 | RUBBER GROMMET | 2 | always use a speed controller with these to dial them in
| TD-250 | S&P |  |  | DD |  | 606 | 0.5 | (241) | 120/1 |  | N/A | 20 | RUBBER GROMMET | 2 | always use a speed controller with these to dial them in
| TD-315 | S&P |  |  | DD |  | 770 | 0.5 | (335) | 120/1 |  | N/A | 31 | RUBBER GROMMET | 2 | always use a speed controller with these to dial them in
| TD-355 | S&P |  |  | DD |  | 1777 | 0.5 | (522) | 120/1 |  | N/A | 43 | RUBBER GROMMET | 2 | always use a speed controller with these to dial them in
| TD-400 | S&P |  |  | DD |  | 2735 | 0.5 | (916) | 120/1 |  | N/A | 78 | RUBBER GROMMET | 2 | always use a speed controller with these to dial them in
| FADE 8-4 | FANTECH |  |  | DD |  | 74 | 0.25 |  |  |  |  | 15
| FADE 10-4 | FANTECH |  |  | DD |  | 132 | 0.37 |  |  |  |  | 15
| FADE 12-4 | FANTECH |  |  | DD |  | 797 | 0.25 |  |  |  |  | 20
| FADE 14-4 | FANTECH |  |  | DD |  | 1295 | 0.25 |  |  |  |  | 20
| FADE 16-4 | FANTECH |  |  | DD |  | 1699 | 0.5 |  |  |  |  | 25
| FADE 18-4 | FANTECH |  |  | DD |  | 2908 | 0.5 |  |  |  |  | 30
| FADE 20-4 | FANTECH |  |  | DD |  | 3445 | 0.5 |  |  |  |  | 45
| FADE 20-6 | FANTECH |  |  | DD |  | 1429 | 0.37 |  |  |  |  | 45
| FADE 22-6 | FANTECH |  |  | DD |  | 4432 | 0.25 |  |  |  |  | 55
| FADE 25-6 | FANTECH |  |  | DD |  | 6557 | 0.25 |  |  |  |  | 65
| Any Fan | [7 empty] | 3/4 | 208/3 | 3.5
| Any Fan | [7 empty] | 1 | 208/3 | 4.6
| Any Fan | [7 empty] | 1.5 | 208/3 | 6.6
| Any Fan | [7 empty] | 2 | 208/3 | 7.5
| Any Fan | [7 empty] | 3 | 208/3 | 10.6
| Any Fan | [7 empty] | 5 | 208/3 | 16.7
| Any Fan | [7 empty] | 7.5 | 208/3 | 24.2
| Any Fan | [7 empty] | 10 | 208/3 | 30.8

## VENTING
RESIDENTIAL VENTING FANS (FURNISHED & INSTALLED BY OTHERS)
# | MFR | MODEL | LOCATION | SERVES | DRIVE | DAMPER | CFM* | SP ("WC) | ELECTRICAL | SONE | NOTES
V / PH
FN-B | TBD | TBD | APARTMENTS | BATHROOM | DIRECT | INT BDD | 20/50 | 0.25 | 120/1 | <1 | 1,2,3
FN-L | TBD | TBD | APARTMENTS | LAUNDRY | DIRECT | INT BDD | 20/50 | 0.25 | 120/1 | <1 | 1,2,3
FN-T | TBD | TBD | APARTMENTS | TRANSFER FAN | DIRECT | INT BDD | 30 | 0.1 | 120/1 | 0.3 | 4
NOTES: 1. PROVIDED & INSTALLED BY OTHERS. FANS SHOWN FOR COORDINATION PURPOSES ONLY. FAN SUBMITTALS TO BE REVIEWED BY MC. 2. CFM VALUE INDICATED CONTINUOUS/INTERMITENT AIRFLOW REQUIREMENTS. EC TO CONFIRM OWNER PREFERENCE AND CONTROLS 3. ONE FAN PER UNIT TO BE DESIGNATED WHOLE HOUSE FAN. FAN TO RUN CONTINUOUS AT WHOLE HOUSE CFM PER TABLE PROVIDED BY MC. FAN TO RAMP UP TO HIGH CFM OF MINIMUM 50 CFM FOR SOURCE SPECIFIC EXHAUST REQUIREMENT. IF INTERMITTENET WHOLE HOUSE VENTILATION CONTROLS ARE USED, CONFIRM OPERATION PER WSMC 403.4.2 SECTION 5 4. FAN TO RUN CONTINUOUS

## OHP
OUTDOOR CONDENSING/HEAT PUMP UNITS
# | MANUF | MODEL | LOCATION | SERVES | COOLING |  | HEATING |  | ELECTRICAL |  |  | LWA (SNS) | WT | ISO. | NOTES
[5 empty] | MBH | SEER (EER) | MBH | HSPF (COP) | V/PH | MCA | MOCP
NOTES: 1. POWER FROM CORRESPONDING OUTDOOR UNIT TO BE WIRED BY EC AND MUST ONLY USE THE WIRE SIZE SHOWN IN THE HEAT PUMP INSTALLATION MANUAL. 3. CONDENSATE PIPING BY EAI. PLUMBER TO PROVIDE RECEPTACLE WITHIN 20' OF UNIT. 4. CONDENSATE PIPING BY OTHERS. 5. HP MOUNTED ON WALL BRACKETS. SEE DETAILS.
NOTES WE TYPICALLY USE (COPY PASTE THE ONES YOU NEED ABOVE): POWER FROM CORRESPONDING OUTDOOR UNIT TO BE WIRED BY EC. POWER WIRING SERVES AS COMMUNICATION BETWEEN DEVICES AND MUST ONLY USE THE WIRE SIZE SHOWN IN THE HEAT PUMP INSTALLATION MANUAL. CONDENSATE PIPING BY EAI. PLUMBER TO PROVIDE RECEPTACLE WITHIN 20' OF UNIT. CONDENSATE PIPING BY OTHERS. HP MOUNTED ON WALL BRACKETS. SEE DETAILS. HP MOUNTED ON ROOF FASTJACK SYSTEM OR SLEEPERS. SEE DETAILS. HP MOUNTED ON MIN 4" CONCRETE HOUSEKEEPING PAD. PAD BY OTHERS. OHP FANS AND PUMPS SET TO CYCLE OFF WHEN THERE IS NO CALL FOR HEATING OR COOLING IN ACCORDANCE WITH 2015 SEC C403.6.2. AUXILARY GROUP R SPACE. ECONOMIZER NOT REQUIRED PER WSEC2015 C403.3 EXCEPTION 6. HP EXCEEDS REQUIREMENTS OF TABLE C403.2.1 BY AT LEAST 15%.

## IHP
FAN COIL UNITS
# | MANUF | MODEL | LOCATION | SERVES | OUTDOOR UNIT MARK | COOLING |  | HEATING |  |  | CFM | OSA | SP ("wg) | ELECTRICAL |  |  | WT | NOTES
[6 empty] | MBH | SEER (EER) | MBH | HSPF (COP) | AUX (KW) |  |  |  | V/PH | MCA | MOCP
NOTES: 1. PROVIDE WITH MHK1 7 DAY PROGRAMMABLE WALL MOUNTED WIRELESS T-STAT. 2. PROVIDE WITH SIMPLE MA WALL MOUNTED WIRELESS THERMOSTAT. 5. CONDENSATE PIPING BY EAI. PLUMBER TO PROVIDE RECEPTACLE WITHIN 20' OF UNIT. 6. CONDENSATE PIPING BY OTHERS. 7. INTEGRAL 22" CONDENSATE LIFT. 8. EAI TO PROVIDE CONDENSATE PUMP. WIRED BY EC. 9. HP MOUNTED ON WALL BRACKETS. SEE DETAILS
NOTES WE TYPICALLY USE (COPY PASTE THE ONES YOU NEED ABOVE): PROVIDE WITH MHK1 7 DAY PROGRAMMABLE WALL MOUNTED WIRELESS T-STAT. PROVIDE WITH SIMPLE MA WALL MOUNTED WIRELESS THERMOSTAT. POWER FROM CORRESPONDING OUTDOOR UNIT TO BE WIRED BY EC. POWER WIRING SERVES AS COMMUNICATION BETWEEN DEVICES AND MUST ONLY USE THE WIRE SIZE SHOWN IN THE HEAT PUMP INSTALLATION MANUAL. CONDENSATE PIPING BY EAI. PLUMBER TO PROVIDE RECEPTACLE WITHIN 20' OF UNIT. CONDENSATE PIPING BY OTHERS. INTEGRAL 22" CONDENSATE LIFT. EAI TO PROVIDE CONDENSATE PUMP. WIRED BY EC. HP MOUNTED ON WALL BRACKETS. SEE DETAILS. HP MOUNTED ON ROOF FASTJACK SYSTEM OR SLEEPERS. SEE DETAILS. HP MOUNTED ON MIN 4" CONCRETE HOUSEKEEPING PAD. PAD BY OTHERS. IHP FANS SET TO CYCLE OFF WHEN THERE IS NO CALL FOR HEATING OR COOLING IN ACCORDANCE WITH 2015 SEC C403.6.2. IHP FAN POWER RATING IS BELOW 0.12W/CFM PER C403.6.2 EXCEPTION 1.

## MINISPLIT
MINISPLIT HEATPUMPS
HP # | FC # | MANUF | MODEL HP | MODEL FC | HEATPUMP LOCATION | FANCOIL LOCATION | SERVES | COOLING |  | HEATING |  | CFM | OSA | SP ("wg) | ELECTRICAL |  |  | HP LWA | HP WT (LBS) | NOTES
[8 empty] | MBH | SEER | MBH | HSPF (COP) |  |  |  | V/PH | MCA | MOCP
NOTES: 1. PROVIDE WITH MHK1 7 DAY PROGRAMMABLE WALL MOUNTED WIRELESS T-STAT.16:26 2. POWER FROM CORRESPONDING OUTDOOR UNIT TO BE WIRED BY EC AND MUST ONLY USE THE WIRE SIZE SHOWN IN THE OHP INSTALLATION MANUAL. 3. CONDENSATE PIPING BY EAI. PLUMBER TO PROVIDE RECEPTACLE WITHIN 20' OF UNIT 4. CONDENSATE PIPING BY OTHER. 5. INTEGRAL 22" CONDENSATE LIFT 6. EAI TO PROVIDE CONDENSATE PUMP. WIRED BY EC. 7. HP MOUNTED ON WALL BRACKETS. SEE DETAILS 8. HP MOUNTED ON ROOF FASTJACK SYSTEM OR SLEEPERS. SEE DETAILS
NOTES WE TYPICALLY USE (COPY PASTE THE ONES YOU NEED ABOVE): PROVIDE WITH MHK1 7 DAY PROGRAMMABLE WALL MOUNTED WIRELESS T-STAT. PROVIDE WITH STANDARD HANDHELD WIRELESS REMOTE CONTROL THERMOSTAT. POWER FROM CORRESPONDING OUTDOOR UNIT TO BE WIRED BY EC. POWER WIRING SERVES AS COMMUNICATION BETWEEN DEVICES AND MUST ONLY USE THE WIRE SIZE SHOWN IN THE HEAT PUMP INSTALLATION MANUAL. CONDENSATE PIPING BY EAI. PLUMBER TO PROVIDE RECEPTACLE WITHIN 20' OF UNIT. CONDENSATE PIPING BY OTHERS. INTEGRAL 22" CONDENSATE LIFT. EAI TO PROVIDE CONDENSATE PUMP. WIRED BY EC. HP MOUNTED ON WALL BRACKETS. SEE DETAILS. HP MOUNTED ON ROOF FASTJACK SYSTEM OR SLEEPERS. SEE DETAILS. HP MOUNTED ON MIN 4" CONCRETE HOUSEKEEPING PAD. PAD BY OTHERS. IHP FANS SET TO CYCLE OFF WHEN THERE IS NO CALL FOR HEATING OR COOLING IN ACCORDANCE WITH 2015 SEC C403.6.2. OHP FANS AND PUMPS SET TO CYCLE OFF WHEN THERE IS NO CALL FOR HEATING OR COOLING IN ACCORDANCE WITH 2015 SEC C403.6.2. IHP FAN POWER RATING IS BELOW 0.12W/CFM PER C403.6.2 EXCEPTION 1. AUXILARY GROUP R SPACE. ECONOMIZER NOT REQUIRED PER SEC2015 C403.3 EXCEPTION 6. HP EXCEEDS REQUIREMENTS OF TABLE C403.2.1 BY AT LEAST 15%.
INSERT LINES WITHIN GRAY ZONE FOR VLOOKUP FUNCTION TO WORK
|  | MITSUBISHI | -- | MSZ-GL06NA |  |  |  | 6 |  | 6 |  | 399 | N/A | N/A | 208/1 | [5 empty] | derated for 60' and seattle temps
|  | MITSUBISHI | MUZ-GL09NA | MSZ-GL09NA |  |  |  | 9 | 24.6 | 9 | 12.8 | 399 | N/A | N/A | 208/1 | 9 | 15 | 50 | 81 |  | derated for 60' and seattle temps
|  | MITSUBISHI | MUZ-GL12NA | MSZ-GL12NA |  |  |  | 12 | 23.1 | 11.5 | 12.5 | 399 | N/A | N/A | 208/1 | 9 | 15 | 51 | 81 |  | derated for 60' and seattle temps
|  | MITSUBISHI | MUZ-GL15NA | MSZ-GL15NA |  |  |  | 14 | 21.6 | 15 | 11.7 | 498 | N/A | N/A | 208/1 | 10 | 20 | 51 | 81 |  | derated for 60' and seattle temps
|  | MITSUBISHI | MUZ-GL18NA | MSZ-GL18NA |  |  |  | 18 | 20.5 | 16.3 | 11.2 | 581 | N/A | N/A | 208/1 | 14 | 20 | 55 | 121 |  | derated for 60' and seattle temps
|  | MITSUBISHI | MUZ-GL24NA | MSZ-GL24NA |  |  |  | 21.5 | 20.5 | 23 | 10 | 661 | N/A | N/A | 208/1 | 17 | 30 | 55 | 119 |  | derated for 60' and seattle temps
|  | MITSUBISHI | MUZ-D30NA | MSZ-D30NA |  |  |  | 29.9 | 14.5 | 21 | 8.2 | 798 | N/A | N/A | 208/1 | 21 | 30 | 57 | 141 |  | derated for 60' and seattle temps
|  | MITSUBISHI | MUZ-D36NA | MSZ-D36NA |  |  |  | 32 | 14.5 | 22 | 8.2 | 798 | N/A | N/A | 208/1 | 21 | 30 | 57 | 141 |  | derated for 60' and seattle temps
|  | MITSUBISHI | SUZ-KA09NA | SLZ-KA09NA |  |  |  | 7.9 | 15 | 7 | 9.6 | 350 | N/A | N/A | 208/1 | 12 | 20 | 50 | 66 |  | derated for 60' and seattle temps
|  | MITSUBISHI | SUZ-KA12NA | SLZ-KA12NA |  |  |  | 11.2 | 15.4 | 8.8 | 9.6 | 390 | N/A | N/A | 208/1 | 12 | 20 | 51 | 77 |  | derated for 60' and seattle temps
|  | MITSUBISHI | SUZ-KA15NA | SLZ-KA15NA |  |  |  | 13.7 | 16 | 11.7 | 9.6 | 390 | N/A | N/A | 208/1 | 12 | 20 | 51 | 80 |  | derated for 60' and seattle temps
|  | MITSUBISHI | SUZ-KA09NA | SEZ-KD09NA |  |  |  | 7.9 | 15 | 7 | 10 | 285 |  | 0.2 | 208/1 | 12 | 20 | 50 | 66 |  | derated for 60' and seattle temps
|  | MITSUBISHI | SUZ-KA12NA | SEZ-KD12NA |  |  |  | 11.2 | 16 | 8.8 | 10 | 349 |  | 0.2 | 208/1 | 12 | 20 | 51 | 77 |  | derated for 60' and seattle temps
|  | MITSUBISHI | SUZ-KA15NA | SEZ-KD15NA |  |  |  | 13.7 | 16 | 11.7 | 9.6 | 390 |  | 0.2 | 208/1 | 12 | 20 | 51 | 80 |  | derated for 60' and seattle temps
|  | MITSUBISHI | SUZ-KA18NA | SEZ-KD18NA |  |  |  | 16.7 | 17.5 | 14 | 10 | 572 |  | 0.2 | 208/1 | 14 | 20 | 56 | 119 |  | derated for 60' and seattle temps
|  | MITSUBISHI | MXZ-3C24NA2 | [5 empty] | 20 |  | 9.8 |  | N/A | N/A | 208/1 | 22.1 | 30 | 55 | 137
[13 empty] | N/A | N/A
|  | MITSUBISHI | MXZ-3C30NA2 | [5 empty] | 19 |  | 10.6 |  | N/A | N/A | 208/1 | 22.1 | 30 | 56 | 137
[13 empty] | N/A | N/A
|  | MITSUBISHI | MXZ-4C36NA2 | [5 empty] | 19.2 |  | 11 |  | N/A | N/A | 208/1 | 22.1 | 30 | 56 | 139
[13 empty] | N/A | N/A
|  | MITSUBISHI | MXZ-5C42NA2 | [5 empty] | 19.7 |  | 10.3 |  | N/A | N/A | 208/1 | 32.5 | 40 | 58 | 189
[13 empty] | N/A | N/A

## FURNACE
GAS FURNACE
# | MANUF | MODEL | LOCATION | SERVES | CFM | OSA | ESP ("WC) | HEATING |  |  |  | ELECTRICAL |  |  | WEIGHT (LBS) | NOTES
[8 empty] | INPUT (MBH) | OUTPUT (MBH) | AFUE | # OF STAGES | V/PH | MCA | MOCP
NOTES: 1. W/ STAINLESS STEEL HEAT EXCHANGER 2. W/ HONEYWELL PRO 8000 TSTAT, SET AT 68F 3. CONDENSATE PIPING BY OTHERS. GAS PIPING AND CONNECTION BY OTHERS 4. TO RUN CONTINUOUS
| ARMSTRONG | A97DSMV110C20S |  |  | 1990 |  | 0.5 | 110 | 107 | 97 | 2 | 120/1 | 12.8 | 20 | 174 |  | DOWNFLOW
LINE VOLTAGE CONTROL WIRING BY OTHERS
LOW VOLTAGE CONTROL WIRING BY EAI

## GASRTU
GAS FIRED ROOFTOP UNIT
# | MANUF | MODEL | LOCATION | SERVES | CFM | OSA | ESP ("WC) | HEATING |  |  | COOLING |  | ELECTRICAL |  |  | WT (LBS) | LWA | NOTES
[8 empty] | INPUT (MBH) | OUTPUT (MBH) | AFUE | TONS | SEER (EER) | V/PH | MCA | MOCP
RTU-1 | CARRIER | 48FCDA05A2A5 | ROOF |  | 1600 | 1600 | 0.5 | 67 | 54 | 81% | 4 | 14 | 208/3 | 26 | 30 | 658 | 78
NOTES: 1. W/ HONEYWELL PRO 8000 TSTAT 2. UNIT MOUNTED ON CURB 3. GAS CONNECTION BY OTHERS 4. UNIT MOUNTED ON SPRING ISOLATION CURB, CURB INFILLED WITH BATT INSULATION (BY OTHERS) 5. W/ 100% OUTSIDE AIR HOOD (ORDER EXTRA FOR YORK) 6. W/ ECONOMIZER HOOD 7. INCLUDE 2 STAGE GAS VALVE W/ STAINLESS STEEL HEATEXCHANGER FOR 100% OSA APPLICATION (YORK UNITS)
| CARRIER |  |  |  | 1200 |  | 0.5 | 75 | 60 | 80 | 3 | 14 | 208/3
| CARRIER |  |  |  | 1600 |  | 0.5 | 100 | 80 | 80 | 4 | 14 | 208/3
| CARRIER |  |  |  | 1990 |  | 0.5 | 125 | 100 | 80 | 5 | 14 | 208/3
| CARRIER |  |  |  | 3000 |  | 0.5 | 190 | 150 | 80 | 7.5 | 14 | 208/3
LINE VOLTAGE CONTROL WIRING BY OTHERS
LOW VOLTAGE CONTROL WIRING BY EAI
Note on F4: Eric Peterson: ABOVE 2000 CFM NEEDS DUCT SMOKE ALARM

## HPRTU
HEATPUMP ROOFTOP UNIT
# | MANUF | MODEL | LOCATION | SERVES | CFM | OSA | ESP ("WC) | HEATING |  | COOLING |  | ELECTRICAL |  |  |  | WT (LBS) | LWA | NOTES | AUX HEAT SIZING CALC FOR OSA ELECTRIC HEATING DURING DEFROST CYCLE
[8 empty] | MBH | HSPF (COP) | TONS | SEER (EER) | V/PH | AUX KW | MCA | MOCP |  |  |  | OUTSIDE TEMP | DISCHARGE TEMP | DERATE 208V=.89 460v=1 | BTU/KW | TON/KW | MIN RATED KW
[19 empty] | 19 | 65 | 0.89 | 3413 | 3.5 | 0
NOTES: 1. W/ HONEYWELL PRO 8000 TSTAT 2. UNIT MOUNTED ON CURB 3. AUXILARY ELECTRIC HEAT IN UNIT 4. UNIT MOUNTED ON SPRING ISOLATION CURB, CURB INFILLED WITH BATT INSULATION (BY OTHERS) 5. W/ 100% OUTSIDE AIR HOOD 6. W/ ECONOMIZER HOOD
| CARRIER |  |  |  | 1200 |  | 0.5 |  |  | 3 | 14 | 208/3 | 17.4571
| CARRIER |  |  |  | 1600 |  | 0.5 |  |  | 4 | 14 | 208/3 | 23.2761
| CARRIER |  |  |  | 1990 |  | 0.5 |  |  | 5 | 14 | 208/3 | 28.9497
| CARRIER |  |  |  | 3000 |  | 0.5 |  |  | 7.5 | 14 | 208/3 | 43.6428
LINE VOLTAGE CONTROL WIRING BY OTHERS
LOW VOLTAGE CONTROL WIRING BY EAI
Note on F4: Eric Peterson: ABOVE 2000 CFM NEEDS DUCT SMOKE ALARM

## GRD
GRILLES, REGISTERS & DIFFUSERS *GENERIC SCHEDULE, ADDITIONAL ITEMS NOT INDICATED ON PLANS/SUBMITTALS SHOWN TO ALLOW FLEXIBILITY FOR FIELD CONDITIONS
# | MANUF | MODEL | SERVICE | MOUNTING | NOTES
A | SHOEMAKER | 904 | SUPPLY | SIDEWALL | 1,2
B | SHOEMAKER | MA | SUPPLY | TBAR/HARDLID | 1,2
C | SHOEMAKER | 905 | RETURN | CEILING/WALL | 1,2
D | SHOEMAKER | RD | SUPPLY | EXPOSED | 1,2
E | SHOEMAKER | 600 | XFR/RETURN | CEILING/WALL | 1,2
F | SHOEMAKER | AFP | SUPPLY | FLOOR | 1,2
NOTES: 1. SEE PLANS FOR DIMENSIONS AND QUANTITY. 2. SEE ARCH PLANS FOR CEILING TYPE. 3. W/OBD.
GRILLES, REGISTERS & DIFFUSERS *GENERIC SCHEDULE, ADDITIONAL ITEMS NOT INDICATED ON PLANS/SUBMITTALS SHOWN TO ALLOW FLEXIBILITY FOR FIELD CONDITIONS
# | MFR | MODEL | SERVICE | MOUNTING | NOTES
A | TITUS | 300RS | SUPPLY | SIDEWALL | 1,2
B | TITUS | MCD | SUPPLY | TBAR/HARDLID | 1,2
C | TITUS | 350RL | RETURN | CEILING/WALL | 1,2
D | TITUS | TMR | SUPPLY | EXPOSED | 1,2
E | TITUS | 50F | XFR/RETURN | CEILING/WALL | 1,2
F | TITUS | CT | SUPPLY | FLOOR | 1,2
NOTES: 1. SEE PLANS FOR DIMENSIONS AND QUANTITY. 2. SEE ARCH PLANS FOR CEILING TYPE. 3. W/OBD.
G | SHOEMAKER | LSD | SPLY/RTN | CEILING/WALL | 1,2,4
4. ORDER LSD-LP TYPE 6 DUCT MOUNT BRACKETS
| ALDES | CSR-S-II | SUPPLY | TBAR/HARDLID | 1,2
| ALDES | CER-S-II | EXHAUST | TBAR/HARDLID | 1,2
GRILLES, REGISTERS & DIFFUSERS *GENERIC SCHEDULE, ADDITIONAL ITEMS NOT INDICATED ON PLANS/SUBMITTALS SHOWN TO ALLOW FLEXIBILITY FOR FIELD CONDITIONS
# | MFR | MODEL | SERVICE | MOUNTING | NOTES
A | PRICE | 520 | SUPPLY | SIDEWALL | 1,2
B | PRICE | SMCD | SUPPLY | TBAR/HARDLID | 1,2
C | PRICE | 530 | RETURN | CEILING/WALL | 1,2
D | PRICE | RCDE | SUPPLY | EXPOSED | 1,2
E | PRICE | 80 | XFR/RETURN | CEILING/WALL | 1,2
F | PRICE | AS | SUPPLY | FLOOR | 1,2
NOTES: 1. SEE PLANS FOR DIMENSIONS AND QUANTITY. 2. SEE ARCH PLANS FOR CEILING TYPE. 3. W/OBD.

## HEATER
ELECTRIC DUCT HEATERS
# | MANUF | MODEL | LOCATION | SERVES | SIZE W(") X L(") | CFM | MIN CFM | DELTA T | STEPS | ELECTRICAL |  |  | CONTROL | NOTES | SIZING CALC
[10 empty] | KW | V/PH | MCA |  |  | OUTSIDE TEMP | DISCHARGE TEMP | 208V DERATE | BTU/KW | MIN RATED SIZE
[15 empty] | 19 | 65 | 0.89 | 3413 | 0
NOTES: 1. HEATER SHOWN FOR SCHEDULING PURPOSES ONLY, SUPPLIED AND INSTALLED BY OTHERS

## ISOLATION
ISOLATION SCHEDULE
ISOLATED EQUIPMENT | ISOLATION TYPE | DEFLECTION PER INCH | LBS PER ISOLATOR | FT OF SOUND LINER NEEDED | QUANTITY | NOTES
BRANCH CONTROLLER | G-1 | N/A | 38 | 0 | 8 | HANG WITH ALLTHREAD. RUBBER GROMMET BELOW AND ABOVE FLANGE
BROAN AE SERIES FANS | G-1 | N/A | 3 | 0 | 8 | RUBBER GROMMET BELOW AND ABOVE FLANGE
BROAN L SERIES FANS | G-1 | N/A | 6 | 0 | 8 | RUBBER GROMMET BELOW AND ABOVE FLANGE
S&P INLINE FANS | G-1 | N/A | 5 | 0 | 8 | RUBBER GROMMET BELOW AND ABOVE FLANGE
TRASH EXHAUST FANS | N-1 | N/A | 45 | 0 | 1 | FAN TO SIT ON GREENHECK CURB WITH NEOPRENE PAD
RES VENTING FANS | G-1 | N/A | 3 | 0 | 8 | RUBBER GROMMET BELOW AND ABOVE FLANGE
WALL MOUNTED OHP (PUMY) | G-1 | N/A | 75 | 0 | 8 | WALL BRACKET INCLUDES NEOPRENE GROMMETS
WALL MOUNTED OHP (PUZ) | G-1 | N/A | 53 | 0 | 8 | WALL BRACKET INCLUDES NEOPRENE GROMMETS
WALL MOUNTED OHP (MUZ/SUZ) | G-1 | N/A | 30 | 0 | 8 | WALL BRACKET INCLUDES NEOPRENE GROMMETS
ROOF MOUNTED OHP | N-1 | N/A | 120 | 0 | 1 | MOUNT ON FAST JACK SUPPORT RACK WITH NEOPRENE PAD
DUCTED FAN COIL | G-1 | N/A | 22 | 0 | 8 | HANG WITH ALLTHREAD. RUBBER GROMMET BELOW AND ABOVE FLANGE
RTU'S | RC-1 | 1" | VARIES | 10 | 1 | FIRST TEN FEET OF SUPPLY AIR TO BE DUCTED
ROOFTOP VRF | B-1/N-1 | N/A | 670 | 0 | 1 | STEEL FRAME BASE WITH NEOPRENE PAD

## LOUVER
LOUVERS/HOODS *GENERIC SCHEDULE, ADDITIONAL ITEMS NOT INDICATED ON PLANS/SUBMITTALS SHOWN TO ALLOW FLEXIBILITY FOR FIELD CONDITIONS
# | MANUF | MODEL | DESCRIPTION | MOUNT | TYPE | MAX INTAKE FPM | SP | NOTES
L-A | POTTORFF | EDD-445 | 4" DEEP LOUVER | SIDEWALL | INTAKE/EXHAUST | 1026 | 0.1 | 1,2,3
L-B | POTTORFF | EFD-245 | 2" DEEP LOUVER | SIDEWALL | INTAKE/EXHAUST | 955 | 0.1 | 1,2,3,5
H-A | ACME | EV | MUSHROOM HOOD | ROOF | EXHAUST | N/A | 0.1 | 1,2,3
H-B | ACME | IV | MUSHROOM HOOD | ROOF | INTAKE | VARIES | 0.1 | 1,2,3
H-C | ACME | LEV | LOUVERED PENTHOUSE | ROOF | EXHAUST | N/A | 0.1 | 1,2,3
H-D | ACME | LIV | LOUVERED PENTHOUSE | ROOF | INTAKE | VARIES | 0.1 | 1,2,3
NOTES: 1. SEE PLANS FOR SIZES AND QUANTITIES. PLANS INDICATE WHOSE SCOPE. 2. STANDARD MILL FINISH; SPECIAL PAINT/COLOR BY OTHERS 3. ARCHITECT TO CONFIRM LOUVER SIZE AND LOCATION, NOTED ON PLANS 4. FOR FUTURE T.I. BLANK OFF AND INSULATE 5. 2" DEEP LOUVER, FOR HEIGHTS <12" OR STOREFRONT
L-C | POTTORFF | EXD-437 | 4" DEEP OPR LOUVER | SIDEWALL | INTAKE/EXHAUST | 955 | 0.1 | 1,2,3,5

## VFD
VARIABLE FREQUENCY DRIVE SCHEDULE
MARK | MANUF | MODEL | LOCATION | SERVES | V / PH | RATED AMPS | NOTES
NOTES: 1. PROVIDE WITH LOCKABLE ENCLOSURE 2. PROVIDE WITH EXTERIOR WEATHER RATED ENCLOSURE. 3. ENCLOSURE FREEZE PROTECTION HEAT TO BE INCLUDED IN UL LISTING. 4. PROVIDED BY MC, INSTALLED BY EC
| MITSUBISHI | FR-D720-070 |  |  | 208/3 | 7
| MITSUBISHI | FR-D720-100 |  |  | 208/3 | 10
| MITSUBISHI | FR-D720-165 |  |  | 208/3 | 16.5
| MITSUBISHI | FR-D720-238 |  |  | 208/3 | 23.8
| MITSUBISHI | FR-D720-318 |  |  | 208/3 | 31.8
FOR EXPLANATION SEE "P:\Engineering\Engineering Tools\Frequently Used Equipment\MITSUBISHI D700 VFD.pdf"
full load amps for different motor sizes
http://www.aic-controls.com/motor-fla
For Smoke Control
| ABB | ACH580-01-06A6-2 |  |  | 208/3 | 6.6
| ABB | ACH580-01-10A6-2 |  |  | 208/3 | 10.6
| ABB | ACH580-01-017A-2 |  |  | 208/3 | 16.7
| ABB | ACH580-01-024A-2 |  |  | 208/3 | 24.2
| ABB | ACH580-01-031A-2 |  |  | 208/3 | 30.8
| ABB | ACH580-01-046A-2 |  |  | 208/3 | 46.2
| ABB | ACH580-01-059A-2 |  |  | 208/3 | 59.4
| ABB | ACH580-01-04A8-4 |  |  | 460/3 | 4.8
| ABB | ACH580-01-07A6-4 |  |  | 460/3 | 7.6
| ABB | ACH580-01-012A-4 |  |  | 460/3 | 12
| ABB | ACH580-01-014A-4 |  |  | 460/3 | 14
| ABB | ACH580-01-023A-4 |  |  | 460/3 | 23
| ABB | ACH580-01-027A-4 |  |  | 460/3 | 27
| ABB | ACH580-01-034A-4 |  |  | 460/3 | 34
Non-Smoke Control
| ABB | ACS320-03U-07A4-2 |  |  | 208/3 | 7.4
| ABB | ACS320-03U-14A6-2 |  |  | 208/3 | 14.6
| ABB | ACS320-03U-19A4-2 |  |  | 208/3 | 19.4
| ABB | ACS320-03U-26A8-2 |  |  | 208/3 | 26.8
| ABB | ACS320-03U-34A1-2 |  |  | 208/3 | 34.1
| ABB | ACS320-03U-03A3-4 |  |  | 460/3 | 3.3
| ABB | ACS320-03U-05A6-4 |  |  | 460/3 | 5.6
| ABB | ACS320-03U-08A8-4 |  |  | 460/3 | 8.8
| ABB | ACS320-03U-12A5-4 |  |  | 460/3 | 12.5
| ABB | ACS320-03U-15A6-4 |  |  | 460/3 | 15.6
| ABB | ACS320-03U-23A1-4 |  |  | 460/3 | 23.1

## SMOKE CONTROL
SMOKE CONTROL EVENT MATRIX
SMOKE CONTROL EQUIPMENT | LOCATION | MONITORED | EMERGENCY POWER | NOMRAL OPERATION | REMARKS | SMOKE ALARM IN ZONE | [10 empty] | <--- EACH SECTION DESCRIBES WHAT HAPPENS IN THE EVENT OF A FIRE ON EACH INDIVIDUAL FLOOR
[6 empty] | LEVEL P1 (VFD MODE 1) | LEVEL 1 (VFD MODE 1) | LEVEL 2 (VFD MODE 1) | LEVEL 3 (VFD MODE 1) | LEVEL 4 (VFD MODE 1) | LEVEL 5 (VFD MODE 1) | LEVEL 6 (VFD MODE 1) | LEVEL 7 (VFD MODE 1) | LEVEL 8 (VFD MODE 1) | LEVEL 9 (VFD MODE 1) | LEVEL 10 (VFD MODE 1)
STAIRWAY PRESSUIZATION
SPF-1: STAIRWELL PRESSUIZATION FAN
SFD-1-1
SFD-1-2
SPF-2: STAIRWELL PRESSUIZATION FAN
MD-2-1
MD-2-2
ELEVATOR LOBBY RELIEF
FSD-1-1
CBD-1-1
MIS. EQUIPMENT
ERV-1: MAIN LOBBY
RTU-1: RES. CORRIDOR
REMARKS: 1. ALL EQUIPMENT THAT IS "ON" OR "OPEN" OR "CLOSED" IN AN EVENT REQUIRES LEGEALLY REQUIRED BACKUP POWER UNLESS OTHERWISE NOTED. 2. ANY ONE COLUMN REPRESENTS A SEPARATE FIRE LIFE SAFETY EVENT. THE AUTMATED SYSTEM IS DESINED FOR AN EVENT IN ONE ZONE ONLY. 3. ALL CONTROL OF FIRE ALARM EQUIPMENT IS DONE BY THE FIRE ALARM SUBCONTRACTOR. 4. EQUIPMENT NOT LISTED IN THIS MATRIX IS NOT AFFECTED DURING A LIFE SAFETY EVENT. 6. ANY CELL LEFT BLANK IN THIS MATRIX INDICATES THE EQUIPMENT OPERATION IS NOT AFFECTED DURING THE EVENT. 7. FOR ALL AIR HANDLERS WITH OUTSIDE AIR, RETURN AND RELIEF DAMPERS INTEGRAL WITH THE UNIT, OPERATION OF THESE DAMPERS TO MATCH THE CORRESPONDING EXTERNAL (TAGGED) DAMPER. 8. DESIGN OF THE SYSTEM FOR INITIATION OF SMOKE CONTROL EVENTS IS BY FIRE LIFE SAFETY CONTRACTOR. 9. GARAGE EXHAUST FANS RAMP TO HIGH ON SMOKE ALARM AT ANY GARAGE FLOOR. 10. HOISTWAY ROOF TOP RELIEF VENT TO OPEN AUTOMATICALLY ONLY WHEN ELEVATOR IS NOT RECALLED TO EITHER THE PRIMARY OR SECONDARY RECALL FLOOR. 11. RATED DAMPERS THAT ARE PART OF THIS SMOKE CONTROL SYSTEM MUST HAVE A MINIMUM CLOSURE TEMPERATURE OF 250F.
REFERENCE: P:\Working Projects\Mirador Ph II (218-0205)\Engineering\Schedules\Mirador Smoke Control Matrix.xlsx